## 00_ERD
GHP Spec DB 정규화 구조 (3NF)
원본: Spec 탭 → 정규화 9개 테이블로 분리 (Lookup 6 + Main 3)
순번 | 테이블명 | 분류 | 행수 | 역할 | 주요 FK
1 | 01_fuel_types | Lookup | 2 | 연료 종류 (LNG/LPG) + 가스압력 범위 | -
2 | 02_refrigerant_types | Lookup | 1 | 냉매 종류 (R410A) | -
3 | 03_engine_types | Lookup | 1 | 엔진 사양 (4기통 2607cc 등 공통 스펙) | -
4 | 04_compressor_types | Lookup | 1 | 압축기 사양 (Scroll x2) | -
5 | 05_fan_types | Lookup | 1 | 송풍기 사양 (프로펠러 BLDC) | -
6 | 06_coolant_pump_types | Lookup | 1 | 냉각수펌프 사양 (BLDC) | -
7 | 07_outdoor_units | Main | 3 | 실외기 단위 사양 (ODU 1대 기준) | engine_type_id, compressor_type_id, fan_type_id, coolant_pump_type_id, refrigerant_type_id
8 | 08_products | Main | 6 | 판매 제품 모델 (단일/듀얼) | -
9 | 09_product_outdoor_units | Link | 6 | products ↔ outdoor_units 다대다 (수량 포함) | product_id, outdoor_unit_id
관계도 (Relationships)
08_products 1 ─── N 09_product_outdoor_units N ─── 1 07_outdoor_units
└ 듀얼 모델은 quantity=2로 표현 (예: GP-W560C2S → GPUW280C2S × 2)
07_outdoor_units N ─── 1 03_engine_types
07_outdoor_units N ─── 1 04_compressor_types
07_outdoor_units N ─── 1 05_fan_types
07_outdoor_units N ─── 1 06_coolant_pump_types
07_outdoor_units N ─── 1 02_refrigerant_types
* 01_fuel_types는 현재 모든 제품이 LNG/LPG 둘 다 지원 → products에 가스압력 직접 보관
* 향후 제품별 지원 연료가 달라지면 product_fuel_types(N:M) 추가 가능
정규화 효과
원본 (Spec_Data Wide): 6행 × 64열 = 384셀, 중복 多, 텍스트 혼합 셀 多
정규화 후 (총 9테이블): 데이터 중복 제거, 모든 수치 단일 타입, FK로 무결성 보장
▶ 듀얼 모델 사양 변경시: outdoor_units 1행만 수정 → 모든 듀얼 제품에 자동 반영
▶ 엔진/압축기 등 공통 부품 사양 변경시: 해당 lookup 1행만 수정
▶ 텍스트로 묶여있던 W×H×D, min~max, x2 같은 표기가 모두 개별 수치 컬럼으로 분리됨

## Spec
항 목 |  | 모델명 | GPUW280C2S | GPUW300C2S | GPUW320C2S | GP-W560C2S | GP-W600C2S | GP-W640C2S
|  | Set 조합 Unit | GPUW280C2S | GPUW300C2S | GPUW320C2S | GPUW280C2S GPUW280C2S | GPUW300C2S GPUW300C2S | GPUW320C2S GPUW320C2S
전 원 |  | 상 / 선 / V / Hz | 1 / 2 / 220 / 60 | 1 / 2 / 220 / 60 | 1 / 2 / 220 / 60 | 1 / 2 / 220 / 60 | 1 / 2 / 220 / 60 | 1 / 2 / 220 / 60
능력 | 냉방 (정격) | kW | 82 | 85 | 90 | 164 | 170 | 180
| 난방 (정격) | kW | 90 | 95 | 100 | 180 | 190 | 200
| 난방한랭지(-15℃) | kW | 69.7 | 72.3 | 76.5 | 139.4 | 144.6 | 153
소비 전력 | 실외기 냉방 (정격) | kW | 2.1 | 2.1 | 2.1 | 4.2 | 4.2 | 4.2
| 실외기 난방 (정격) | kW | 1.2 | 1.2 | 1.2 | 2.4 | 2.4 | 2.4
| 실외기 난방한랭지(-15℃) | kW | 0.6 | 0.6 | 0.6 | 1.2 | 1.2 | 1.2
| 실내기 냉방 (정격) | kW | 1.9 | 2 | 2.1 | 3.8 | 4 | 4.2
| 실내기 난방 (정격) | kW | 1.6 | 1.6 | 1.5 | 3.2 | 3.2 | 3
| 실내기 난방한랭지(-15℃) | kW | 1.4 | 1.4 | 1.4 | 2.8 | 2.8 | 2.8
사용연료 | 가스종 | - | LNG 13A / LPG | LNG 13A / LPG | LNG 13A / LPG | LNG 13A / LPG | LNG 13A / LPG | LNG 13A / LPG
| 가스압력 | kPa | 2.0 ~ 2.5 / 2.3 ~ 3.3 | 2.0 ~ 2.5 / 2.3 ~ 3.3 | 2.0 ~ 2.5 / 2.3 ~ 3.3 | 2.0 ~ 2.5 / 2.3 ~ 3.3 | 2.0 ~ 2.5 / 2.3 ~ 3.3 | 2.0 ~ 2.5 / 2.3 ~ 3.3
연료 소비량 | 냉방 (정격) | kW | 53.9 | 56.8 | 60 | 53.9 + 53.9 | 56.8 + 56.8 | 60.0 + 60.0
| 난방 (정격) | kW | 54 | 57.3 | 61 | 54.0 + 54.0 | 57.3 + 57.3 | 61.0 + 61.0
| 난방한랭지(-15℃) | kW | 63 | 66 | 71 | 63.0 + 63.0 | 66.0 + 66.0 | 71.0 + 71.0
효율 | 냉방효율(COP) | - | 1.42 | 1.4 | 1.4 | 1.42 | 1.4 | 1.4
| 난방효율(COP) | - | 1.58 | 1.58 | 1.57 | 1.58 | 1.58 | 1.57
| 난방한랭지효율(COP) | - | 1.07 | 1.06 | 1.05 | 1.07 | 1.06 | 1.05
운전 전류 | 냉방 (정격) | A | 12 | 12 | 12 | 24 | 24 | 24
| 난방 (정격) | A | 6.6 | 6.6 | 6.6 | 13.2 | 13.2 | 13.2
| 시동전류 | A | 40 | 40 | 40 | 40.0 x 2 | 40.0 x 2 | 40.0 x 2
엔진 | 형식 | - | 수랭식 4사이클 4기통 | 수랭식 4사이클 4기통 | 수랭식 4사이클 4기통 | 수랭식 4사이클 4기통 | 수랭식 4사이클 4기통 | 수랭식 4사이클 4기통
| 기관수 x 내경 x 행정 | mm | 4 x ø91.1 x 4 | 4 x ø91.1 x 4 | 4 x ø91.1 x 4 | 4 x ø91.1 x 4 | 4 x ø91.1 x 4 | 4 x ø91.1 x 4
| 배기량 | cc/Rev | 2 607 | 2 607 | 2 607 | 2 607 | 2 607 | 2 607
| 정격출력 | PS | 30.8 (1400rpm 기준) | 30.8 (1400rpm 기준) | 30.8 (1400rpm 기준) | 30.8 (1400rpm 기준) | 30.8 (1400rpm 기준) | 30.8 (1400rpm 기준)
| 윤활유 종류 | - | KIXX CNG 10W/40 | KIXX CNG 10W/40 | KIXX CNG 10W/40 | KIXX CNG 10W/40 | KIXX CNG 10W/40 | KIXX CNG 10W/40
| 윤활유 봉입량 | L | 38 | 38 | 38 | 38 x 2 | 38 x 2 | 38 x 2
| 회전 속도 범위 | rev/min | 900 ~ 2 000 (한랭지 2 300) | 900 ~ 2 000 (한랭지 2 300) | 900 ~ 2 000 (한랭지 2 300) | 900 ~ 2 000 (한랭지 2 300) | 900 ~ 2 000 (한랭지 2 300) | 900 ~ 2 000 (한랭지 2 300)
| 기동모터 출력 | - | DC 2.2 kW | DC 2.2 kW | DC 2.2 kW | DC 2.2 kW | DC 2.2 kW | DC 2.2 kW
| 기동방식 | - | AC/DC 변환식, DC 스타터 | AC/DC 변환식, DC 스타터 | AC/DC 변환식, DC 스타터 | AC/DC 변환식, DC 스타터 | AC/DC 변환식, DC 스타터 | AC/DC 변환식, DC 스타터
엔진냉각수 | 냉각수 봉입량 | ℓ | 26 | 26 | 26 | 26 x 2 | 26 x 2 | 26 x 2
| 농도(에틸렌글리콜/물) | % (V/V) | 50 | 50 | 50 | 50 | 50 | 50
| 동결온도 | ℃ | -35 | -35 | -35 | -35 | -35 | -35
압축기 | 형식 | - | Scroll x 2 | Scroll x 2 | Scroll x 2 | Scroll x 2 | Scroll x 2 | Scroll x 2
| 냉동기유 봉입량 | L | 6.4 (FVC68L) | 6.4 (FVC68L) | 6.4 (FVC68L) | 6.4 x 2 (FVC68L) | 6.4 x 2 (FVC68L) | 6.4 x 2 (FVC68L)
| 크랭크 케이스 히터 | - | 40 x 2 | 40 x 2 | 40 x 2 | (40 x 2) x 2 | 40 x 2 | 40 x 2
| Piston 범위 | cc/Rev | 120 + 120 | 120 + 120 | 120 + 120 | 120 + 120 | 120 + 120 | 120 + 120
송풍기 | 형식 | - | 프로펠러식 | 프로펠러식 | 프로펠러식 | 프로펠러식 | 프로펠러식 | 프로펠러식
| 풍량 | m3/min | 430 | 430 | 430 | 430 x 2 | 430 x 2 | 430 x 2
| 정격 출력 | kW x No. | 1.5 x 2 | 1.5 x 2 | 1.5 x 2 | (1.5 x 2) x 2 | (1.5 x 2) x 2 | (1.5 x 2) x 2
냉각수펌프 | 종류 | - | BLDC | BLDC | BLDC | BLDC | BLDC | BLDC
| 소비전력 | kW | 0.165 | 0.165 | 0.165 | 0.165 x 2 | 0.165 | 0.165
제품 치수 | 본체 치수(W × H × D) | mm | 1 800 x 2 180 x 960 | 1 800 x 2 180 x 960 | 1 800 x 2 180 x 960 | (1 800 x 2 180 x 960) x 2 | (1 800 x 2 180 x 960) x 2 | (1 800 x 2 180 x 960) x 2
| 포장 치수(W × H × D) | mm | 1 830 x 2 360 x 1 090 | 1 830 x 2 360 x 1 090 | 1 830 x 2 360 x 1 090 | (1 830 x 2 360 x 1 090) x 2 | (1 830 x 2 360 x 1 090) x 2 | (1 830 x 2 360 x 1 090) x 2
제품 중량 | 본체 중량 | kg | 915 | 915 | 915 | 915 x 2 | 915 x 2 | 915 x 2
| 포장 중량 | kg | 930 | 930 | 930 | 930 x 2 | 930 x 2 | 930 x 2
보호 장치 | 고압보호 | - | ○ | ○ | ○ | ○ | ○ | ○
| 토출온도 제어장치 | - | ○ | ○ | ○ | ○ | ○ | ○
배관경 | 냉매 액관 | ø,mm | 19.05 | 19.05 | 19.05 | 19.05 | 19.05 | 22.2
| 냉매 가스관 | ø,mm | 34.9 | 34.9 | 34.9 | 41.3 | 41.3 | 44.5
| 연료 가스 배관 | inch | R 3/4 (수나사) | R 3/4 (수나사) | R 3/4 (수나사) | R 3/4 x 2 (수나사) | R 3/4 x 2 (수나사) | R 3/4 x 2 (수나사)
| 배기구경 | ø,mm | 145 | 145 | 145 | 145 | 145 | 145
| 배기 드레인 배관 | ø,mm | 31.2 (Hose) | 31.2 (Hose) | 31.2 (Hose) | 31.2 x 2 (Hose) | 31.2 x 2 (Hose) | 31.2 x 2 (Hose)
소음 | 냉방 | dB(A) | 60 | 60 | 60 | 63 | 63 | 63
| 난방 | dB(A) | 60 | 60 | 60 | 63 | 63 | 63
냉매 | 냉매명 | - | R410A | R410A | R410A | R410A | R410A | R410A
| 충진량(제품봉입량) | kg | 18 | 18 | 18 | 18.0 x 2 | 18.0 x 2 | 18.0 x 2
연결 전선 | 전원선( H07RN-F, 접지포함) | ㎟ x cores | 4.0 x 3C | 4.0 x 3C | 4.0 x 3C | (4.0 x 3C) x 2 또는 10.0 x 3C | (4.0 x 3C) x 2 또는 10.0 x 3C | (4.0 x 3C) x 2 또는 10.0 x 3C
| 통신선( VCTF - SB) | ㎟ x cores | 0.75 ~ 1.5 x 2C | 0.75 ~ 1.5 x 2C | 0.75 ~ 1.5 x 2C | 0.75 ~ 1.5 x 2C | 0.75 ~ 1.5 x 2C | 0.75 ~ 1.5 x 2C
법정 냉동능력 |  | RT | 9.35 | 9.5 | 9.65 | 18.7 | 19 | 19.3
차단기(ELCB) |  | A | 30 | 30 | 30 | 30 x 2 또는 60 x 1 | 30 x 2 또는 60 x 1 | 30 x 2 또는 60 x 1
최대 연결 가능 실내기수 |  | 대 | 53 | 55 | 58 | 64 | 64 | 64

## Spec_Data
no | model_name | set_combination_unit | capacity_cooling_rated_kw | capacity_heating_rated_kw | capacity_heating_cold_region_minus15c_kw | power_consumption_outdoor_cooling_rated_kw | power_consumption_outdoor_heating_rated_kw | power_consumption_outdoor_heating_cold_region_kw | power_consumption_indoor_cooling_rated_kw | power_consumption_indoor_heating_rated_kw | power_consumption_indoor_heating_cold_region_kw | fuel_gas_type | fuel_gas_pressure_kpa | fuel_consumption_cooling_rated_kw | fuel_consumption_heating_rated_kw | fuel_consumption_heating_cold_region_kw | efficiency_cooling_cop | efficiency_heating_cop | efficiency_heating_cold_region_cop | operating_current_cooling_rated_a | operating_current_heating_rated_a | operating_current_starting_a | engine_type | engine_cylinders_bore_stroke_mm | engine_displacement_cc_per_rev | engine_rated_output_ps | engine_lubricant_type | engine_lubricant_capacity_l | engine_rotation_speed_range_rpm | engine_starter_motor_output | engine_starting_method | engine_coolant_capacity_l | engine_coolant_concentration_ethylene_glycol_water_pct | engine_coolant_freezing_temperature_c | compressor_type | compressor_oil_capacity_l | compressor_crankcase_heater | compressor_piston_range_cc_per_rev | fan_type | fan_airflow_m3_per_min | fan_rated_output_kw_x_no | coolant_pump_type | coolant_pump_power_consumption_kw | product_dimensions_body_wxhxd_mm | product_dimensions_package_wxhxd_mm | product_weight_body_kg | product_weight_package_kg | protection_device_high_pressure | protection_device_discharge_temp_control | piping_refrigerant_liquid_mm | piping_refrigerant_gas_mm | piping_fuel_gas_inch | piping_exhaust_outlet_mm | piping_exhaust_drain_mm | noise_cooling_db_a | noise_heating_db_a | refrigerant_name | refrigerant_charge_amount_kg | wiring_power_cable_mm2_x_cores | wiring_communication_cable_mm2_x_cores | legal_refrigeration_capacity_rt | circuit_breaker_elcb_a | max_connectable_indoor_units
No. | 모델명 | Set 조합 Unit | 능력 - 냉방 (정격) (kW) | 능력 - 난방 (정격) (kW) | 능력 - 난방한랭지(-15℃) (kW) | 소비 전력 - 실외기 냉방 (정격) (kW) | 소비 전력 - 실외기 난방 (정격) (kW) | 소비 전력 - 실외기 난방한랭지(-15℃) (kW) | 소비 전력 - 실내기 냉방 (정격) (kW) | 소비 전력 - 실내기 난방 (정격) (kW) | 소비 전력 - 실내기 난방한랭지(-15℃) (kW) | 사용연료 - 가스종 | 사용연료 - 가스압력 (kPa) | 연료 소비량 - 냉방 (정격) (kW) | 연료 소비량 - 난방 (정격) (kW) | 연료 소비량 - 난방한랭지(-15℃) (kW) | 효율 - 냉방효율(COP) | 효율 - 난방효율(COP) | 효율 - 난방한랭지효율(COP) | 운전 전류 - 냉방 (정격) (A) | 운전 전류 - 난방 (정격) (A) | 운전 전류 - 시동전류 (A) | 엔진 - 형식 | 엔진 - 기관수 x 내경 x 행정 (mm) | 엔진 - 배기량 (cc/Rev) | 엔진 - 정격출력 (PS) | 엔진 - 윤활유 종류 | 엔진 - 윤활유 봉입량 (L) | 엔진 - 회전 속도 범위 (rev/min) | 엔진 - 기동모터 출력 | 엔진 - 기동방식 | 엔진냉각수 - 냉각수 봉입량 (ℓ) | 엔진냉각수 - 농도(에틸렌글리콜/물) (% (V/V)) | 엔진냉각수 - 동결온도 (℃) | 압축기 - 형식 | 압축기 - 냉동기유 봉입량 (L) | 압축기 - 크랭크 케이스 히터 | 압축기 - Piston 범위 (cc/Rev) | 송풍기 - 형식 | 송풍기 - 풍량 (m3/min) | 송풍기 - 정격 출력 (kW x No.) | 냉각수펌프 - 종류 | 냉각수펌프 - 소비전력 (kW) | 제품 치수 - 본체 치수(W × H × D) (mm) | 제품 치수 - 포장 치수(W × H × D) (mm) | 제품 중량 - 본체 중량 (kg) | 제품 중량 - 포장 중량 (kg) | 보호 장치 - 고압보호 | 보호 장치 - 토출온도 제어장치 | 배관경 - 냉매 액관 (ø,mm) | 배관경 - 냉매 가스관 (ø,mm) | 배관경 - 연료 가스 배관 (inch) | 배관경 - 배기구경 (ø,mm) | 배관경 - 배기 드레인 배관 (ø,mm) | 소음 - 냉방 (dB(A)) | 소음 - 난방 (dB(A)) | 냉매 - 냉매명 | 냉매 - 충진량(제품봉입량) (kg) | 연결 전선 - 전원선( H07RN-F, 접지포함) (㎟ x cores) | 연결 전선 - 통신선( VCTF - SB) (㎟ x cores) | 법정 냉동능력 (RT) | 차단기(ELCB) (A) | 최대 연결 가능 실내기수 (대)
1 | GPUW280C2S | GPUW280C2S | 82 | 90 | 69.7 | 2.1 | 1.2 | 0.6 | 1.9 | 1.6 | 1.4 | LNG 13A / LPG | 2.0 ~ 2.5 / 2.3 ~ 3.3 | 53.9 | 54 | 63 | 1.42 | 1.58 | 1.07 | 12 | 6.6 | 40 | 수랭식 4사이클 4기통 | 4 x ø91.1 x 4 | 2 607 | 30.8 (1400rpm 기준) | KIXX CNG 10W/40 | 38 | 900 ~ 2 000 (한랭지 2 300) | DC 2.2 kW | AC/DC 변환식, DC 스타터 | 26 | 50 | -35 | Scroll x 2 | 6.4 (FVC68L) | 40 x 2 | 120 + 120 | 프로펠러식 | 430 | 1.5 x 2 | BLDC | 0.165 | 1 800 x 2 180 x 960 | 1 830 x 2 360 x 1 090 | 915 | 930 | ○ | ○ | 19.05 | 34.9 | R 3/4 (수나사) | 145 | 31.2 (Hose) | 60 | 60 | R410A | 18 | 4.0 x 3C | 0.75 ~ 1.5 x 2C | 9.35 | 30 | 53
2 | GPUW300C2S | GPUW300C2S | 85 | 95 | 72.3 | 2.1 | 1.2 | 0.6 | 2 | 1.6 | 1.4 | LNG 13A / LPG | 2.0 ~ 2.5 / 2.3 ~ 3.3 | 56.8 | 57.3 | 66 | 1.4 | 1.58 | 1.06 | 12 | 6.6 | 40 | 수랭식 4사이클 4기통 | 4 x ø91.1 x 4 | 2 607 | 30.8 (1400rpm 기준) | KIXX CNG 10W/40 | 38 | 900 ~ 2 000 (한랭지 2 300) | DC 2.2 kW | AC/DC 변환식, DC 스타터 | 26 | 50 | -35 | Scroll x 2 | 6.4 (FVC68L) | 40 x 2 | 120 + 120 | 프로펠러식 | 430 | 1.5 x 2 | BLDC | 0.165 | 1 800 x 2 180 x 960 | 1 830 x 2 360 x 1 090 | 915 | 930 | ○ | ○ | 19.05 | 34.9 | R 3/4 (수나사) | 145 | 31.2 (Hose) | 60 | 60 | R410A | 18 | 4.0 x 3C | 0.75 ~ 1.5 x 2C | 9.5 | 30 | 55
3 | GPUW320C2S | GPUW320C2S | 90 | 100 | 76.5 | 2.1 | 1.2 | 0.6 | 2.1 | 1.5 | 1.4 | LNG 13A / LPG | 2.0 ~ 2.5 / 2.3 ~ 3.3 | 60 | 61 | 71 | 1.4 | 1.57 | 1.05 | 12 | 6.6 | 40 | 수랭식 4사이클 4기통 | 4 x ø91.1 x 4 | 2 607 | 30.8 (1400rpm 기준) | KIXX CNG 10W/40 | 38 | 900 ~ 2 000 (한랭지 2 300) | DC 2.2 kW | AC/DC 변환식, DC 스타터 | 26 | 50 | -35 | Scroll x 2 | 6.4 (FVC68L) | 40 x 2 | 120 + 120 | 프로펠러식 | 430 | 1.5 x 2 | BLDC | 0.165 | 1 800 x 2 180 x 960 | 1 830 x 2 360 x 1 090 | 915 | 930 | ○ | ○ | 19.05 | 34.9 | R 3/4 (수나사) | 145 | 31.2 (Hose) | 60 | 60 | R410A | 18 | 4.0 x 3C | 0.75 ~ 1.5 x 2C | 9.65 | 30 | 58
4 | GP-W560C2S | GPUW280C2S GPUW280C2S | 164 | 180 | 139.4 | 4.2 | 2.4 | 1.2 | 3.8 | 3.2 | 2.8 | LNG 13A / LPG | 2.0 ~ 2.5 / 2.3 ~ 3.3 | 53.9 + 53.9 | 54.0 + 54.0 | 63.0 + 63.0 | 1.42 | 1.58 | 1.07 | 24 | 13.2 | 40.0 x 2 | 수랭식 4사이클 4기통 | 4 x ø91.1 x 4 | 2 607 | 30.8 (1400rpm 기준) | KIXX CNG 10W/40 | 38 x 2 | 900 ~ 2 000 (한랭지 2 300) | DC 2.2 kW | AC/DC 변환식, DC 스타터 | 26 x 2 | 50 | -35 | Scroll x 2 | 6.4 x 2 (FVC68L) | (40 x 2) x 2 | 120 + 120 | 프로펠러식 | 430 x 2 | (1.5 x 2) x 2 | BLDC | 0.165 x 2 | (1 800 x 2 180 x 960) x 2 | (1 830 x 2 360 x 1 090) x 2 | 915 x 2 | 930 x 2 | ○ | ○ | 19.05 | 41.3 | R 3/4 x 2 (수나사) | 145 | 31.2 x 2 (Hose) | 63 | 63 | R410A | 18.0 x 2 | (4.0 x 3C) x 2 또는 10.0 x 3C | 0.75 ~ 1.5 x 2C | 18.7 | 30 x 2 또는 60 x 1 | 64
5 | GP-W600C2S | GPUW300C2S GPUW300C2S | 170 | 190 | 144.6 | 4.2 | 2.4 | 1.2 | 4 | 3.2 | 2.8 | LNG 13A / LPG | 2.0 ~ 2.5 / 2.3 ~ 3.3 | 56.8 + 56.8 | 57.3 + 57.3 | 66.0 + 66.0 | 1.4 | 1.58 | 1.06 | 24 | 13.2 | 40.0 x 2 | 수랭식 4사이클 4기통 | 4 x ø91.1 x 4 | 2 607 | 30.8 (1400rpm 기준) | KIXX CNG 10W/40 | 38 x 2 | 900 ~ 2 000 (한랭지 2 300) | DC 2.2 kW | AC/DC 변환식, DC 스타터 | 26 x 2 | 50 | -35 | Scroll x 2 | 6.4 x 2 (FVC68L) | 40 x 2 | 120 + 120 | 프로펠러식 | 430 x 2 | (1.5 x 2) x 2 | BLDC | 0.165 | (1 800 x 2 180 x 960) x 2 | (1 830 x 2 360 x 1 090) x 2 | 915 x 2 | 930 x 2 | ○ | ○ | 19.05 | 41.3 | R 3/4 x 2 (수나사) | 145 | 31.2 x 2 (Hose) | 63 | 63 | R410A | 18.0 x 2 | (4.0 x 3C) x 2 또는 10.0 x 3C | 0.75 ~ 1.5 x 2C | 19 | 30 x 2 또는 60 x 1 | 64
6 | GP-W640C2S | GPUW320C2S GPUW320C2S | 180 | 200 | 153 | 4.2 | 2.4 | 1.2 | 4.2 | 3 | 2.8 | LNG 13A / LPG | 2.0 ~ 2.5 / 2.3 ~ 3.3 | 60.0 + 60.0 | 61.0 + 61.0 | 71.0 + 71.0 | 1.4 | 1.57 | 1.05 | 24 | 13.2 | 40.0 x 2 | 수랭식 4사이클 4기통 | 4 x ø91.1 x 4 | 2 607 | 30.8 (1400rpm 기준) | KIXX CNG 10W/40 | 38 x 2 | 900 ~ 2 000 (한랭지 2 300) | DC 2.2 kW | AC/DC 변환식, DC 스타터 | 26 x 2 | 50 | -35 | Scroll x 2 | 6.4 x 2 (FVC68L) | 40 x 2 | 120 + 120 | 프로펠러식 | 430 x 2 | (1.5 x 2) x 2 | BLDC | 0.165 | (1 800 x 2 180 x 960) x 2 | (1 830 x 2 360 x 1 090) x 2 | 915 x 2 | 930 x 2 | ○ | ○ | 22.2 | 44.5 | R 3/4 x 2 (수나사) | 145 | 31.2 x 2 (Hose) | 63 | 63 | R410A | 18.0 x 2 | (4.0 x 3C) x 2 또는 10.0 x 3C | 0.75 ~ 1.5 x 2C | 19.3 | 30 x 2 또는 60 x 1 | 64

## 01_fuel_types
id | code | name_ko | pressure_min_kpa | pressure_max_kpa
1 | LNG_13A | LNG 13A | 2 | 2.5
2 | LPG | LPG | 2.3 | 3.3

## 02_refrigerant_types
id | code | name
1 | R410A | R410A

## 03_engine_types
id | code | cooling_method | stroke_cycle | cylinders | bore_mm | stroke_mm | displacement_cc | rated_output_ps | rated_output_rpm | lubricant_type | lubricant_capacity_l | rpm_min | rpm_max | rpm_max_cold_region | starter_motor_output | starting_method
1 | ENG_4CYL_2607CC | 수랭식 | 4 | 4 | 91.1 | 4 | 2607 | 30.8 | 1400 | KIXX CNG 10W/40 | 38 | 900 | 2000 | 2300 | DC 2.2 kW | AC/DC 변환식, DC 스타터

## 04_compressor_types
id | code | type | qty_per_unit | oil_capacity_l | oil_model | crankcase_heater_w | crankcase_heater_qty | piston_range_cc_per_rev
1 | SCROLL_x2 | Scroll | 2 | 6.4 | FVC68L | 40 | 2 | 120 + 120

## 05_fan_types
id | code | type | motor_type | airflow_m3_min | rated_output_kw | rated_output_qty
1 | PROPELLER_BLDC | 프로펠러식 | BLDC | 430 | 1.5 | 2

## 06_coolant_pump_types
id | code | type | power_consumption_kw
1 | BLDC_PUMP | BLDC | 0.165

## 07_outdoor_units
id | model_code | capacity_cooling_kw | capacity_heating_kw | capacity_heating_cold_kw | power_outdoor_cooling_kw | power_outdoor_heating_kw | power_outdoor_heating_cold_kw | power_indoor_cooling_kw | power_indoor_heating_kw | power_indoor_heating_cold_kw | fuel_consumption_cooling_kw | fuel_consumption_heating_kw | fuel_consumption_heating_cold_kw | efficiency_cooling_cop | efficiency_heating_cop | efficiency_heating_cold_cop | operating_current_cooling_a | operating_current_heating_a | starting_current_a | engine_type_id | engine_coolant_capacity_l | engine_coolant_eg_water_pct | engine_freezing_temp_c | compressor_type_id | fan_type_id | coolant_pump_type_id | body_width_mm | body_height_mm | body_depth_mm | package_width_mm | package_height_mm | package_depth_mm | body_weight_kg | package_weight_kg | has_high_pressure_protection | has_discharge_temp_control | pipe_refrigerant_liquid_mm | pipe_refrigerant_gas_mm | fuel_gas_pipe_spec | exhaust_outlet_mm | exhaust_drain_mm | exhaust_drain_type | noise_cooling_db | noise_heating_db | refrigerant_type_id | refrigerant_charge_kg | legal_refrigeration_capacity_rt
1 | GPUW280C2S | 82 | 90 | 69.7 | 2.1 | 1.2 | 0.6 | 1.9 | 1.6 | 1.4 | 53.9 | 54 | 63 | 1.42 | 1.58 | 1.07 | 12 | 6.6 | 40 | 1 | 26 | 50 | -35 | 1 | 1 | 1 | 1800 | 2180 | 960 | 1830 | 2360 | 1090 | 915 | 930 | TRUE | TRUE | 19.05 | 34.9 | R 3/4 (수나사) | 145 | 31.2 | Hose | 60 | 60 | 1 | 18 | 9.35
2 | GPUW300C2S | 85 | 95 | 72.3 | 2.1 | 1.2 | 0.6 | 2 | 1.6 | 1.4 | 56.8 | 57.3 | 66 | 1.4 | 1.58 | 1.06 | 12 | 6.6 | 40 | 1 | 26 | 50 | -35 | 1 | 1 | 1 | 1800 | 2180 | 960 | 1830 | 2360 | 1090 | 915 | 930 | TRUE | TRUE | 19.05 | 34.9 | R 3/4 (수나사) | 145 | 31.2 | Hose | 60 | 60 | 1 | 18 | 9.5
3 | GPUW320C2S | 90 | 100 | 76.5 | 2.1 | 1.2 | 0.6 | 2.1 | 1.5 | 1.4 | 60 | 61 | 71 | 1.4 | 1.57 | 1.05 | 12 | 6.6 | 40 | 1 | 26 | 50 | -35 | 1 | 1 | 1 | 1800 | 2180 | 960 | 1830 | 2360 | 1090 | 915 | 930 | TRUE | TRUE | 19.05 | 34.9 | R 3/4 (수나사) | 145 | 31.2 | Hose | 60 | 60 | 1 | 18 | 9.65

## 08_products
id | model_code | phase | wire | voltage_v | frequency_hz | lng_pressure_min_kpa | lng_pressure_max_kpa | lpg_pressure_min_kpa | lpg_pressure_max_kpa | power_cable_mm2 | power_cable_cores | power_cable_alt_mm2 | power_cable_alt_cores | comm_cable_mm2_min | comm_cable_mm2_max | comm_cable_cores | circuit_breaker_primary_a | circuit_breaker_primary_qty | circuit_breaker_alt_a | circuit_breaker_alt_qty | max_indoor_units
1 | GPUW280C2S | 1 | 2 | 220 | 60 | 2 | 2.5 | 2.3 | 3.3 | 4 | 3 |  |  | 0.75 | 1.5 | 2 | 30 | 1 |  |  | 53
2 | GPUW300C2S | 1 | 2 | 220 | 60 | 2 | 2.5 | 2.3 | 3.3 | 4 | 3 |  |  | 0.75 | 1.5 | 2 | 30 | 1 |  |  | 55
3 | GPUW320C2S | 1 | 2 | 220 | 60 | 2 | 2.5 | 2.3 | 3.3 | 4 | 3 |  |  | 0.75 | 1.5 | 2 | 30 | 1 |  |  | 58
4 | GP-W560C2S | 1 | 2 | 220 | 60 | 2 | 2.5 | 2.3 | 3.3 | 4 | 3 | 10 | 3 | 0.75 | 1.5 | 2 | 30 | 2 | 60 | 1 | 64
5 | GP-W600C2S | 1 | 2 | 220 | 60 | 2 | 2.5 | 2.3 | 3.3 | 4 | 3 | 10 | 3 | 0.75 | 1.5 | 2 | 30 | 2 | 60 | 1 | 64
6 | GP-W640C2S | 1 | 2 | 220 | 60 | 2 | 2.5 | 2.3 | 3.3 | 4 | 3 | 10 | 3 | 0.75 | 1.5 | 2 | 30 | 2 | 60 | 1 | 64

## 09_product_outdoor_units
id | product_id | outdoor_unit_id | quantity
1 | 1 | 1 | 1
2 | 2 | 2 | 1
3 | 3 | 3 | 1
4 | 4 | 1 | 2
5 | 5 | 2 | 2
6 | 6 | 3 | 2